## Optima 250
Modbus protokol for ES950 Optima 250
Mode: | RTU | (MSB first)
Standard: | Modbus application protokol specification V1.1a Modbus over serial lin V1.02
WWW adresse | Modbus.org
Baud | 0=Modbus Off, 1=9600, 2=19200 | default | 0
Start bits | 1 | default | 1
Data bits | 8 | default | 8
Stop Bits | 1 | default | 1
Parity | Even | default | Even
Address | 1-247 | default | 1
Registers Map
Support function | 1,2,3,4,5,6,17
Register number | Data description | R/W | Length | Units | Valid response | Remarks
0x0000 | Relay 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0001 | Relay 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0002 | Relay 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0003 | Relay 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0004 | Relay 5 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0005 | Relay 6 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0006 | Relay 7 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0007 | Relay 8 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0008 | Relay 9 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0009 | Relay 10 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0010 | Relay 11 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0011 | Not Used Digital out 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0012 | Not Used Digital out 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0013 | Not Used Digital out 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0014 | Not Used Digital out 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0000 | Hygrostat | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0001 | Start/stop | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0002 | Not Used Digital in1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0003 | Not Used Digital in2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0004 | Not Used Digital in3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0005 | Not Used Digital in4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
3x0000 | T1 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0001 | T2 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0002 | T3 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0003 | T4 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0004 | T5 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0005 | T6 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0006 | T7 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0007 | T8 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0008 | T9 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0009 | T2 Panel | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0010 | Messured Humidity | R | 1 | UINT16 | 0-100% | 0=0%, 100=100%
3x0011 | Humidity calculated setpoint | R | 1 | UINT16 | 0-100% | 0=0%, 100=100%
3x0101 | Alarm | R | 1 | UINT16 | Bits
3x0102 | Inlet fan | R |  | UINT16 | 0-100%
3x0103 | Extract fan | R | 1 | UINT16 | 0-100%
3x0104 | Bypass | R | 1 | UINT16 | 0-100%
3x0105 | Watervalve | R | 1 | UINT16 | 0-100%
3x0106 | Humidity FAN control +/- | R | 1 | UINT16 | -100% - 100% | 0=-100%, 200=100%
3x0107 | Bypass ON/OFF | R | 1 | UINT16 | 0=OFF, 1=ON
3x0108 | Inlet fan RPM | R | 1 | UINT16 | 0-9999
3x0109 | Extract fan RPM | R | 1 | UINT16 | 0-9999
3x0200 | Programme Version Controller | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0201 | Programme Version Display | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0202 | Sub Version Controller | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0203 | Sub Version Display | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0204 | ModbusVersion | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0205 | Sub ModbusVersion | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
[11 empty] | Display | Display
Group0 | [6 empty] | Min | Max | Offset | Resolution | Min+offset | Max+offset
4x0000 | 01) Temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 200 | 100 | 0.1 | 10 | 30
4x0001 | 02) Preheat (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0002 | 03) Reheat (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0003 | 04) Timer level 3-4 (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0004 | 05) Filter change (mdr) | R/W | 1 | UINT16 |  |  | 0 | 6 | 0 | 1 | 0 | 6
4x0005 | 06) Humidity (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0006 | 10) Level 1 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0007 | 11) Level 2 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0008 | 12) Level 3 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0009 | 13) Level 1 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0010 | 14) Level 2 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0011 | 15) Level 3 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0012 | 16) T2 adjustment (°C) | R/W | 1 | UINT16 |  |  | 0 | 50 | -50 | 0.1 | -5 | 0
4x0013 | 17) Level 3-4 (hour) | R/W | 1 | UINT16 |  |  | 1 | 9 | 0 | 1 | 1 | 9
4x0014 | 18) Filter change autostop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0015 | 19) Regform (0=Rum,1=indbl, 2=udsug) | R/W | 1 | UINT16 |  |  | 0 | 2 | 0 | 1 | 0 | 2
4x0016 | 20) Preheat Temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | -150 | 0.1 | -15 | 0
4x0017 | 21) Bypass max (°C) | R/W | 1 | UINT16 |  |  | 10 | 100 | 0 | 0.1 | 1 | 10
4x0018 | 22) Water reg interval (sec) | R/W | 1 | UINT16 |  |  | 1 | 250 | 0 | 1 | 1 | 250
4x0019 | 23) Power reg interval (min) | R/W | 1 | UINT16 |  |  | 1 | 30 | 0 | 1 | 1 | 30
4x0020 | 24) Frost reduction (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0021 | 25) Frost (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0022 | 26) Frost Default (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0023 | 27) Aux. relay R9 | R/W | 1 | UINT16 |  |  | 0 | 5 | 0 | 1 | 0 | 5
4x0024 | 28) Stop unit (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0025 | 29) End bypass at low fresh air (°C) | R/W | 1 | UINT16 |  |  | 0 | 20 | 0 | 1 | 0 | 20
4x0026 | 30) Modbus mode (0=OFF, 1=9600, 2=19200) | R/W | 1 | UINT16 |  | 0=Modbus Off, 1=9600, 2=19200 | 0 | 2 | 0 | 1 | 0 | 2
4x0027 | 31) Modbus address | R/W | 1 | UINT16 |  |  | 1 | 247 | 0 | 1 | 1 | 247
4x0028 | 32) Humidity max temp. | R/W | 1 | UINT16 |  |  | 5 | 25 | 0 | 1 | 5 | 25
4x0029 | 33) Humidity max value | R/W | 1 | UINT16 |  |  | 35 | 85 | 0 | 1 | 35 | 85
4x0030 | 34) Humidity Fan speed | R/W | 1 | UINT16 |  |  | 5 | 30 | 0 | 1 | 5 | 30
4x0031 | 35) Humidity regulation | R/W | 1 | UINT16 |  |  | 1 | 60 | 0 | 1 | 1 | 60
4x0032
4x0033
4x0034
4x0035
4x0036
4x0037
4x0038
4x0039
4x0040
4x0041
4x0042
4x0043
4x0044
4x0045
4x0046
4x0047
4x0048
4x0049
4x0050
4x0051
4x0052
4x0053
4x0054
4x0055
4x0056
4x0057
4x0058
4x0059
Group1
4x0100 | Panel fan mode speed switch | R/W | 1 | UINT16 | 0-4 | 0=Off, 1=S1, 2=S2, 3=S3, 4=S4
4x0102 | Function K3 Heat ON | R/W | 1 | UINT16 | 0-1 | 0=Off, 1=ON
4x0106 | Function K2 Timer | R/W | 1 | UINT16 | 0-9 | 0=Off, 1-9 = 1-9Hour
4x0105 | Common ResetFilter | R/W | 1 | UINT16 | 0-1 | 1=reset filter
Group2
4x0200 | Hour | R/W |  | UINT16 | 0-23
4x0201 | Minute | R/W |  | UINT16 | 0-59
4x0202 | Day | R/W |  | UINT16 | 1-7
4x0203 | Date | R/W |  | UINT16 | 1-31
4x0204 | Month | R/W |  | UINT16 | 1-12
4x0205 | Year | R/W |  | UINT16 | 0-99 | 0= jahr 2000
Group3
4x0500 | 1 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0501 | 2 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0502 | 3 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0503 | 4 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0504 | 5 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0505 | 6 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0506 | 7 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0507 | 8 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0508 | 9 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0509 | 10 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0510 | 11 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0511 | 12 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0512 | 13 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0513 | 14 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0514 | 15 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0515 | 16 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0516 | 17 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0517 | 18 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0518 | 19 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0519 | 20 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0520 | 21 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0521 | 22 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0522 | 23 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0523 | 24 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0524 | 25 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0525 | 26 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0526 | 27 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0527 | 28 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0528 | 29 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0529 | 30 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0530 | 31 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0531 | 32 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0532 | 33 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0533 | 34 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0534 | 35 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0535 | 36 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0536 | 37 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0537 | 38 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0538 | 39 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0539 | 40 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0540 | 41 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0541 | 42 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0542 | 43 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0543 | 44 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0544 | 45 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0545 | 46 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0546 | 47 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0547 | 48 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0548 | 49 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0549 | 50 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0550 | 51 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0551 | 52 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0552 | 53 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0553 | 54 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0554 | 55 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0555 | 56 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0556 | 57 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0557 | 58 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0558 | 59 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0559 | 60 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0560 | 61 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0561 | 62 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0562 | 63 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0563 | 64 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0564 | 65 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0565 | 66 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0566 | 67 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0567 | 68 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0568 | 69 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0569 | 70 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
Group4
4x0600 | 1 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0601 | 2 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0602 | 3 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0603 | 4 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0604 | 5 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0605 | 6 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0606 | 7 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0607 | 8 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0608 | 9 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0609 | 10 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0610 | 11 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0611 | 12 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0612 | 13 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0613 | 14 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0614 | 15 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0615 | 16 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0616 | 17 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0617 | 18 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0618 | 19 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0619 | 20 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0620 | 21 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0621 | 22 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0622 | 23 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0623 | 24 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0624 | 25 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0625 | 26 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0626 | 27 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0627 | 28 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0628 | 29 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0629 | 30 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0630 | 31 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0631 | 32 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0632 | 33 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0633 | 34 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0634 | 35 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0635 | 36 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0636 | 37 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0637 | 38 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0638 | 39 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0639 | 40 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0640 | 41 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0641 | 42 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0642 | 43 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0643 | 44 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0644 | 45 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0645 | 46 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0646 | 47 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0647 | 48 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0648 | 49 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0649 | 50 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0650 | 51 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0651 | 52 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0652 | 53 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0653 | 54 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0654 | 55 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0655 | 56 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0656 | 57 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0657 | 58 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0658 | 59 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0659 | 60 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0660 | 61 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0661 | 62 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0662 | 63 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0663 | 64 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0664 | 65 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0665 | 66 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0666 | 67 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0667 | 68 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0668 | 69 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0669 | 70 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction

## Optima 251
Modbus protokol for ES950 Optima 251 |  |  | ver 3.7a5
Mode: | RTU | (MSB first)
Standard: | Modbus application protokol specification V1.1a Modbus over serial lin V1.02
WWW adresse | Modbus.org
Baud | 0=Modbus Off, 1=9600, 2=19200 | default | 0
Start bits | 1 | default | 1
Data bits | 8 | default | 8
Stop Bits | 1 | default | 1
Parity | Even | default | Even
Address | 1-247 | default | 1
Registers Map
Support function | 1,2,3,4,5,6,17
Register number | Data description | R/W | Length | Units | Valid response | Remarks
0x0000 | Relay 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0001 | Relay 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0002 | Relay 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0003 | Relay 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0004 | Relay 5 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0005 | Relay 6 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0006 | Relay 7 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0007 | Relay 8 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0008 | Relay 9 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0009 | Relay 10 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0010 | Relay 11 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0011 | Not Used Digital out 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0012 | Not Used Digital out 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0013 | Not Used Digital out 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0014 | Not Used Digital out 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0000 | Hygrostat | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0001 | Start/stop | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0002 | Not Used Digital in1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0003 | Not Used Digital in2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0004 | Not Used Digital in3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0005 | Not Used Digital in4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
3x0000 | T1 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0001 | T2 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0002 | T3 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0003 | T4 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0004 | T5 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0005 | T6 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0006 | T7 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0007 | T8 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0008 | T9 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0009 | T2 Panel | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0010 | Messured Humidity | R | 1 | UINT16 | 0-100% | 0=0%, 100=100%
3x0011 | Humidity calculated setpoint | R | 1 | UINT16 | 0-100% | 0=0%, 100=100%
3x0012 | T10 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0013 | T11 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0014 | T12 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0015 | T13 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0016 | brand_alarm_com_status | R | 1 | UINT16 | 0-255 | Bit0=Err at SPJ 1, Bit1=Err at SPJ 2, Bit3=Err at SPJ 3, Bit4=Err at SPJ 4 Bit5-6=Err at box 1, Bit7-8=Err at Box 2
3x0017 | brand_testresultat | R | 1 | UINT16 | 0-255 | Bit0=Err at SPJ 1, Bit1=Err at SPJ 2, Bit3=Err at SPJ 3, Bit4=Err at SPJ 4 Bit7=Test OK
3x0018 | brand_test_dato | R | 1 | UINT16 | 1-31
3x0019 | brand_test_maaned | R | 1 | UINT16 | 1-12
3x0020 | brand_test_aar | R | 1 | UINT16 | 0-99
3x0021 | brand_test_time | R | 1 | UINT16 | 0-23
3x0022 | brand_test_minut | R | 1 | UINT16 | 0-59
3x0023 | brand_test_err | R | 1 | UINT16 | 0-255 | Bit0=Err at SPJ 1, Bit1=Err at SPJ 2, Bit3=Err at SPJ 3, Bit4=Err at SPJ 4
3x0101 | Alarm | R | 1 | UINT16 | Bits
3x0102 | Inlet fan | R |  | UINT16 | 0-100%
3x0103 | Extract fan | R | 1 | UINT16 | 0-100%
3x0104 | Bypass | R | 1 | UINT16 | 0-100%
3x0105 | Watervalve | R | 1 | UINT16 | 0-100%
3x0106 | Humidity FAN control +/- | R | 1 | UINT16 | -100% - 100% | 0=-100%, 200=100%
3x0107 | Bypass ON/OFF | R | 1 | UINT16 | 0=OFF, 1=ON
3x0108 | Inlet fan RPM | R | 1 | UINT16 | 0-9999
3x0109 | Extract fan RPM | R | 1 | UINT16 | 0-9999
3x0200 | Programme Version Controller | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0201 | Programme Version Display | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0202 | Sub Version Controller | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0203 | Sub Version Display | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0204 | ModbusVersion | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0205 | Sub ModbusVersion | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
[11 empty] | Display | Display
Group0 | [6 empty] | Min | Max | Offset | Resolution | Min+offset | Max+offset
4x0000 | 01) Temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 200 | 100 | 0.1 | 10 | 30
4x0001 | 02) Preheat (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0002 | 03) Reheat (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0003 | 04) Timer level 3-4 (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0004 | 05) Filter change (mdr) | R/W | 1 | UINT16 |  |  | 0 | 6 | 0 | 1 | 0 | 6
4x0005 | 06) Humidity (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0006 | 10) Level 1 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0007 | 11) Level 2 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0008 | 12) Level 3 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0009 | 13) Level 1 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0010 | 14) Level 2 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0011 | 15) Level 3 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0012 | 16) T2 adjustment (°C) | R/W | 1 | UINT16 |  |  | 0 | 50 | -50 | 0.1 | -5 | 0
4x0013 | 17) Level 3-4 (hour) | R/W | 1 | UINT16 |  |  | 1 | 9 | 0 | 1 | 1 | 9
4x0014 | 18) Filter change autostop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0015 | 19) Regform (0=Rum,1=indbl, 2=udsug) | R/W | 1 | UINT16 |  |  | 0 | 2 | 0 | 1 | 0 | 2
4x0016 | 20) Preheat Temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | -150 | 0.1 | -15 | 0
4x0017 | 21) Bypass max (°C) | R/W | 1 | UINT16 |  |  | 10 | 100 | 0 | 0.1 | 1 | 10
4x0018 | 22) Water reg interval (sec) | R/W | 1 | UINT16 |  |  | 1 | 250 | 0 | 1 | 1 | 250
4x0019 | 23) Power reg interval (min) | R/W | 1 | UINT16 |  |  | 1 | 30 | 0 | 1 | 1 | 30
4x0020 | 24) Frost reduction (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0021 | 25) Frost (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0022 | 26) Frost Default (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0023 | 27) Aux. relay R9 | R/W | 1 | UINT16 |  |  | 0 | 5 | 0 | 1 | 0 | 5
4x0024 | 28) Stop unit (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0025 | 29) End bypass at low fresh air (°C) | R/W | 1 | UINT16 |  |  | 0 | 20 | 0 | 1 | 0 | 20
4x0026 | 30) Modbus mode (0=OFF, 1=9600, 2=19200) | R/W | 1 | UINT16 |  | 0=Modbus Off, 1=9600, 2=19200 | 0 | 2 | 0 | 1 | 0 | 2
4x0027 | 31) Modbus address | R/W | 1 | UINT16 |  |  | 1 | 247 | 0 | 1 | 1 | 247
4x0028 | 32) Humidity max temp. | R/W | 1 | UINT16 |  |  | 5 | 25 | 0 | 1 | 5 | 25
4x0029 | 33) Humidity max value | R/W | 1 | UINT16 |  |  | 35 | 85 | 0 | 1 | 35 | 85
4x0030 | 34) Humidity Fan speed | R/W | 1 | UINT16 |  |  | 5 | 30 | 0 | 1 | 5 | 30
4x0031 | 35) Humidity regulation | R/W | 1 | UINT16 |  |  | 1 | 60 | 0 | 1 | 1 | 60
4x0032 | 36) Højre/Venstre | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0033 | 37) Forvarme PI P | R/W | 1 | UINT16 |  |  | 1 | 255 | 0 | 1 | 1 | 255
4x0034 | 38) Forvarme PI I | R/W | 1 | UINT16 |  |  | 1 | 255 | 0 | 1 | 1 | 255
4x0035 | 39) Forvarme Reg (sek) | R/W | 1 | UINT16 |  |  | 10 | 120 | 0 | 1 | 10 | 120
4x0036 | 40) Eftervarme (°C) | R/W | 1 | UINT16 |  |  | 0 | 250 | 150 | 0.1 | 15 | 40
4x0037 | 41) Eftervarme PI P | R/W | 1 | UINT16 |  |  | 1 | 255 | 0 | 1 | 1 | 255
4x0038 | 42) Eftervarme PI I | R/W | 1 | UINT16 |  |  | 1 | 255 | 0 | 1 | 1 | 255
4x0039 | 43) Eftervarm Reg (sek) | R/W | 1 | UINT16 |  |  | 10 | 120 | 0 | 1 | 10 | 120
4x0040 | 44) Behovsstyring | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0041 | 45) Brandspjæld (0=OFF, 1-4 antal) | R/W | 1 | UINT16 |  |  | 0 | 4 | 0 | 1 | 0 | 4
4x0042 | 46) Brandspjæld test (1=Test) | R/W | 1 | UINT16 |  |  | 0 | 2 | 0 | 1 | 0 | 2
4x0043 | 47) Brand test dag (0=Mandag, 7=Søndag) | R/W | 1 | UINT16 |  |  | 1 | 7 | 0 | 1 | 1 | 7
4x0044 | 48) Brand test Time (0-23) | R/W | 1 | UINT16 |  |  | 0 | 23 | 0 | 1 | 0 | 23
4x0045
4x0046
4x0047
4x0048
4x0049
4x0050
4x0051
4x0052
4x0053
4x0054
4x0055
4x0056
4x0057
4x0058
4x0059
Group1
4x0100 | Panel fan mode speed switch | R/W | 1 | UINT16 | 0-4 | 0=Off, 1=S1, 2=S2, 3=S3, 4=S4
4x0102 | Function K3 Heat ON | R/W | 1 | UINT16 | 0-1 | 0=Off, 1=ON
4x0106 | Function K2 Timer | R/W | 1 | UINT16 | 0-9 | 0=Off, 1-9 = 1-9Hour
4x0105 | Common ResetFilter | R/W | 1 | UINT16 | 0-1 | 1=reset filter
Group2
4x0200 | Hour | R/W |  | UINT16 | 0-23
4x0201 | Minute | R/W |  | UINT16 | 0-59
4x0202 | Day | R/W |  | UINT16 | 1-7
4x0203 | Date | R/W |  | UINT16 | 1-31
4x0204 | Month | R/W |  | UINT16 | 1-12
4x0205 | Year | R/W |  | UINT16 | 0-99 | 0= jahr 2000
Group3
4x0500 | 1 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0501 | 2 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0502 | 3 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0503 | 4 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0504 | 5 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0505 | 6 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0506 | 7 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0507 | 8 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0508 | 9 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0509 | 10 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0510 | 11 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0511 | 12 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0512 | 13 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0513 | 14 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0514 | 15 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0515 | 16 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0516 | 17 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0517 | 18 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0518 | 19 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0519 | 20 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0520 | 21 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0521 | 22 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0522 | 23 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0523 | 24 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0524 | 25 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0525 | 26 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0526 | 27 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0527 | 28 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0528 | 29 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0529 | 30 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0530 | 31 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0531 | 32 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0532 | 33 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0533 | 34 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0534 | 35 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0535 | 36 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0536 | 37 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0537 | 38 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0538 | 39 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0539 | 40 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0540 | 41 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0541 | 42 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0542 | 43 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0543 | 44 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0544 | 45 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0545 | 46 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0546 | 47 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0547 | 48 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0548 | 49 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0549 | 50 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0550 | 51 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0551 | 52 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0552 | 53 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0553 | 54 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0554 | 55 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0555 | 56 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0556 | 57 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0557 | 58 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0558 | 59 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0559 | 60 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0560 | 61 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0561 | 62 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0562 | 63 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0563 | 64 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0564 | 65 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0565 | 66 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0566 | 67 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0567 | 68 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0568 | 69 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0569 | 70 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
Group4
4x0600 | 1 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0601 | 2 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0602 | 3 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0603 | 4 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0604 | 5 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0605 | 6 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0606 | 7 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0607 | 8 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0608 | 9 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0609 | 10 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0610 | 11 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0611 | 12 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0612 | 13 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0613 | 14 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0614 | 15 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0615 | 16 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0616 | 17 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0617 | 18 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0618 | 19 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0619 | 20 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0620 | 21 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0621 | 22 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0622 | 23 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0623 | 24 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0624 | 25 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0625 | 26 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0626 | 27 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0627 | 28 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0628 | 29 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0629 | 30 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0630 | 31 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0631 | 32 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0632 | 33 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0633 | 34 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0634 | 35 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0635 | 36 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0636 | 37 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0637 | 38 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0638 | 39 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0639 | 40 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0640 | 41 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0641 | 42 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0642 | 43 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0643 | 44 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0644 | 45 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0645 | 46 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0646 | 47 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0647 | 48 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0648 | 49 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0649 | 50 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0650 | 51 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0651 | 52 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0652 | 53 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0653 | 54 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0654 | 55 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0655 | 56 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0656 | 57 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0657 | 58 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0658 | 59 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0659 | 60 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0660 | 61 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0661 | 62 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0662 | 63 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0663 | 64 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0664 | 65 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0665 | 66 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0666 | 67 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0667 | 68 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0668 | 69 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0669 | 70 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction

## Optima 260
Modbus protokol for OPT260
Mode: | RTU | (MSB first)
Standard: | Modbus application protokol specification V1.1a Modbus over serial lin V1.02
WWW adresse | Modbus.org
Baud | 0=Modbus Off, 1=9600, 2=19200 | default | 0
Start bits | 1 | default | 1
Data bits | 8 | default | 8
Stop Bits | 1 | default | 1
Parity | Even | default | Even
Address | 1-247 | default | 1
Registers Map
Support function | 3,4,6,17 | [11 empty] | Nabto Information
[13 empty] | Type | Object | Read Adress
Register number | Data description | R/W | Length | Units | Valid response | Remarks
3x0000 | T1 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C | [6 empty] | Datapoint | 0 | 0
3x0001 | T2 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C | [6 empty] | Datapoint | 0 | 1
3x0002 | T3 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C | [6 empty] | Datapoint | 0 | 2
3x0003 | T4 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C | [6 empty] | Datapoint | 0 | 3
3x0004 | Forvarme | R | 1 | UINT16 |  | 0-100 | [6 empty] | Datapoint | 0 | 4
3x0005 | Eftervarme | R | 1 | UINT16 |  | 0-100 | [6 empty] | Datapoint | 0 | 5
3x0006 | T7 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C | [6 empty] | Datapoint | 0 | 6
3x0007 | T8 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C | [6 empty] | Datapoint | 0 | 7
3x0008 | T9 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C | [6 empty] | Datapoint | 0 | 8
3x0009 | Indblæs ventilator | R | 1 | UINT16 |  | 0-100 | [6 empty] | Datapoint | 0 | 9
3x0010 | Udsug ventilator | R | 1 | UINT16 |  | 0-100 | [6 empty] | Datapoint | 0 | 10
3x0011 | Bypass ventil | R | 1 | UINT16 |  | 0-100 | [6 empty] | Datapoint | 0 | 11
3x0012 | Varmtvand ventil | R | 1 | UINT16 |  | 0-100 | [6 empty] | Datapoint | 0 | 12
3x0013 | Fugt | R | 1 | UINT16 |  | 0-100 | [6 empty] | Datapoint | 0 | 13
3x0014 | Fugt Set | R | 1 | UINT16 |  | 0-100 | [6 empty] | Datapoint | 0 | 14
3x0015 | Digital (Look at Alarmbit page) | R | 1 | UINT16 | [8 empty] | Datapoint | 0 | 15
[11 empty] | Display | Display
[7 empty] | Min | Max | Offset | Resolution | Min+offset | Max+offset | Type | Object | R/W Adress
4x0000 | Hastighed valg | R/W | 1 | UINT16 |  |  | 0 | 4 | 0 | 1 | 0 | 4 | Setpoint | 0 | 0
4x0001 | Heat valg (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 1
4x0002 | 01) Temperatur (°C) | R/W | 1 | UINT16 |  |  | 0 | 200 | 100 | 0.1 | 10 | 30 | Setpoint | 0 | 2
4x0003 | 02) Forvarme (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 3
4x0004 | 04) Timer trin 3-4 (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 4
4x0005 | 05) Filterskift (mdr) | R/W | 1 | UINT16 |  |  | 0 | 12 | 0 | 1 | 0 | 12 | Setpoint | 0 | 5
4x0006 | 06) Fugtstyring (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 6
4x0007 | 10) Trin 1 indblæs (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100 | Setpoint | 0 | 7
4x0008 | 11) Trin 2 indbæls (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100 | Setpoint | 0 | 8
4x0009 | 12) Trin 3 indbæls (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100 | Setpoint | 0 | 9
4x0010 | 13) Trin 1 udsug (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100 | Setpoint | 0 | 10
4x0011 | 14) Trin 2 udsug (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100 | Setpoint | 0 | 11
4x0012 | 15) Trin 3 udsug (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100 | Setpoint | 0 | 12
4x0013 | 16) T2 justering (°C) | R/W | 1 | UINT16 |  |  | 0 | 50 | -50 | 0.1 | -5 | 0 | Setpoint | 0 | 13
4x0014 | 17) Timer trin 3-4 (timer) | R/W | 1 | UINT16 |  |  | 1 | 9 | 0 | 1 | 1 | 9 | Setpoint | 0 | 14
4x0015 | 18) Filterskift autostop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 15
4x0016 | 19) Regform (0=Rum,1=indbl, 2=udsug) | R/W | 1 | UINT16 |  |  | 0 | 2 | 0 | 1 | 0 | 2 | Setpoint | 0 | 16
4x0017 | 20) Forvarme temperatur (°C) | R/W | 1 | UINT16 |  |  | 0 | 250 | -150 | 0.1 | -15 | 10 | Setpoint | 0 | 17
4x0018 | 21) Bypass max (°C) | R/W | 1 | UINT16 |  |  | 10 | 100 | 0 | 0.1 | 1 | 10 | Setpoint | 0 | 18
4x0019 | 22) Regulator vand interval (sek) | R/W | 1 | UINT16 |  |  | 1 | 250 | 0 | 1 | 1 | 250 | Setpoint | 0 | 19
4x0020 | 23) Regulator el interval (min) | R/W | 1 | UINT16 |  |  | 1 | 30 | 0 | 1 | 1 | 30 | Setpoint | 0 | 20
4x0021 | 24) Frostreduktion (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10 | Setpoint | 0 | 21
4x0022 | 25) Vandfrost (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 22
4x0023 | 26) Vandfrost setpunkt (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10 | Setpoint | 0 | 23
4x0024 | 27) Hjælperelæ R9 | R/W | 1 | UINT16 |  |  | 0 | 5 | 0 | 1 | 0 | 5 | Setpoint | 0 | 24
4x0025 | 28) Anlæg stop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 25
4x0026 | 29) Sluk bypass ved lav friskluft (°C) | R/W | 1 | UINT16 |  |  | 0 | 20 | 0 | 1 | 0 | 20 | Setpoint | 0 | 26
4x0027 | 30) Modbus mode (0=OFF, 1=9600, 2=19200) | R/W | 1 | UINT16 |  | 0=Modbus Off, 1=9600, 2=19200 | 0 | 2 | 0 | 1 | 0 | 2 | Setpoint | 0 | 27
4x0028 | 31) Modbus adresse | R/W | 1 | UINT16 |  |  | 1 | 247 | 0 | 1 | 1 | 247 | Setpoint | 0 | 28
4x0029 | 32) Fugt max temp (°C) | R/W | 1 | UINT16 |  |  | 5 | 25 | 0 | 1 | 5 | 25 | Setpoint | 0 | 29
4x0030 | 33) Fugt max værdi (%) | R/W | 1 | UINT16 |  |  | 35 | 85 | 0 | 1 | 35 | 85 | Setpoint | 0 | 30
4x0031 | 34) Fugt vent hast (%) | R/W | 1 | UINT16 |  |  | 5 | 30 | 0 | 1 | 5 | 30 | Setpoint | 0 | 31
4x0032 | 35) fugt regulerings hyppighed (min) | R/W | 1 | UINT16 |  |  | 1 | 60 | 0 | 1 | 1 | 60 | Setpoint | 0 | 32
4x0033 | 36) Højre/Venstre | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 33
4x0034 | 37) Forvarme PI P | R/W | 1 | UINT16 |  |  | 1 | 255 | 0 | 1 | 1 | 255 | Setpoint | 0 | 34
4x0035 | 38) Forvarme PI I | R/W | 1 | UINT16 |  |  | 1 | 255 | 0 | 1 | 1 | 255 | Setpoint | 0 | 35
4x0036 | 39) Forvarme Reg (sek) | R/W | 1 | UINT16 |  |  | 10 | 120 | 0 | 1 | 10 | 120 | Setpoint | 0 | 36
4x0037 | 40) Eftervarme (°C) | R/W | 1 | UINT16 |  |  | 0 | 250 | 150 | 0.1 | 15 | 40 | Setpoint | 0 | 37
4x0038 | 41) Eftervarme PI P | R/W | 1 | UINT16 |  |  | 1 | 255 | 0 | 1 | 1 | 255 | Setpoint | 0 | 38
4x0039 | 42) Eftervarme PI I | R/W | 1 | UINT16 |  |  | 1 | 255 | 0 | 1 | 1 | 255 | Setpoint | 0 | 39
4x0040 | 43) Eftervarm Reg (sek) | R/W | 1 | UINT16 |  |  | 10 | 120 | 0 | 1 | 10 | 120 | Setpoint | 0 | 40
4x0041 | 44) Display model (0=OFF, 1=OPT100, 2=Knap) | R/W | 1 | UINT16 |  |  | 0 | 2 | 0 | 1 | 0 | 2 | Setpoint | 0 | 41
4x0042 | 45) Boost tid 1 (min) | R/W | 1 | UINT16 |  |  | 0 | 250 | 0 | 1 | 0 | 250 | Setpoint | 0 | 42
4x0043 | 46) Boost tid 2 (min) | R/W | 1 | UINT16 |  |  | 0 | 250 | 0 | 1 | 0 | 250 | Setpoint | 0 | 43
4x0044 | 47) Boost tid 3 (min) | R/W | 1 | UINT16 |  |  | 0 | 250 | 0 | 1 | 0 | 250 | Setpoint | 0 | 44
4x0045 | 48) Kalender ON (OFF/ON) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 45
4x0046 | 49) CO2 control | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 1 | Setpoint | 0 | 46
4x0047 | 50) Filter reset | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1 | Setpoint | 0 | 47
Clock | [12 empty] | Type | Object | Adress
4x0200 | Hour | R/W |  | UINT16 | 0-23 | [7 empty] | Setpoint | 0 | 48
4x0201 | Minute | R/W |  | UINT16 | 0-59 | [7 empty] | Setpoint | 0 | 49
4x0202 | Day | R/W |  | UINT16 | 1-7 | [7 empty] | Setpoint | 0 | 50
4x0203 | Date | R/W |  | UINT16 | 1-31 | [7 empty] | Setpoint | 0 | 51
4x0204 | Month | R/W |  | UINT16 | 1-12 | [7 empty] | Setpoint | 0 | 52
4x0205 | Year | R/W |  | UINT16 | 0-99 | 0= år 2000 | [6 empty] | Setpoint | 0 | 53
Kalender Timer + minutter | Eks. Timer x 256+min -> 23*256+59=5888+59=5947 | [5 empty] | Dag | Skift | Min Timer:0 Min:0 | Max Timer:23 Min:59 |  |  | Type | Object | Adress
4x0500 | 1 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 1 |  |  |  |  | Setpoint | 0 | 120
4x0501 | 2 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 2 |  |  |  |  | Setpoint | 0 | 121
4x0502 | 3 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 3 |  |  |  |  | Setpoint | 0 | 122
4x0503 | 4 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 4 |  |  |  |  | Setpoint | 0 | 123
4x0504 | 5 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 5 |  |  |  |  | Setpoint | 0 | 124
4x0505 | 6 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 6 |  |  |  |  | Setpoint | 0 | 125
4x0506 | 7 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 7 |  |  |  |  | Setpoint | 0 | 126
4x0507 | 8 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 8 |  |  |  |  | Setpoint | 0 | 127
4x0508 | 9 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 9 |  |  |  |  | Setpoint | 0 | 128
4x0509 | 10 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Mandag | skift 10 |  |  |  |  | Setpoint | 0 | 129
4x0510 | 11 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 1 |  |  |  |  | Setpoint | 0 | 130
4x0511 | 12 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 2 |  |  |  |  | Setpoint | 0 | 131
4x0512 | 13 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 3 |  |  |  |  | Setpoint | 0 | 132
4x0513 | 14 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 4 |  |  |  |  | Setpoint | 0 | 133
4x0514 | 15 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 5 |  |  |  |  | Setpoint | 0 | 134
4x0515 | 16 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 6 |  |  |  |  | Setpoint | 0 | 135
4x0516 | 17 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 7 |  |  |  |  | Setpoint | 0 | 136
4x0517 | 18 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 8 |  |  |  |  | Setpoint | 0 | 137
4x0518 | 19 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 9 |  |  |  |  | Setpoint | 0 | 138
4x0519 | 20 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Tirsdag | skift 10 |  |  |  |  | Setpoint | 0 | 139
4x0520 | 21 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 1 |  |  |  |  | Setpoint | 0 | 140
4x0521 | 22 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 2 |  |  |  |  | Setpoint | 0 | 141
4x0522 | 23 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 3 |  |  |  |  | Setpoint | 0 | 142
4x0523 | 24 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 4 |  |  |  |  | Setpoint | 0 | 143
4x0524 | 25 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 5 |  |  |  |  | Setpoint | 0 | 144
4x0525 | 26 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 6 |  |  |  |  | Setpoint | 0 | 145
4x0526 | 27 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 7 |  |  |  |  | Setpoint | 0 | 146
4x0527 | 28 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 8 |  |  |  |  | Setpoint | 0 | 147
4x0528 | 29 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 9 |  |  |  |  | Setpoint | 0 | 148
4x0529 | 30 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Onsdag | skift 10 |  |  |  |  | Setpoint | 0 | 149
4x0530 | 31 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 1 |  |  |  |  | Setpoint | 0 | 150
4x0531 | 32 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 2 |  |  |  |  | Setpoint | 0 | 151
4x0532 | 33 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 3 |  |  |  |  | Setpoint | 0 | 152
4x0533 | 34 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 4 |  |  |  |  | Setpoint | 0 | 153
4x0534 | 35 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 5 |  |  |  |  | Setpoint | 0 | 154
4x0535 | 36 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 6 |  |  |  |  | Setpoint | 0 | 155
4x0536 | 37 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 7 |  |  |  |  | Setpoint | 0 | 156
4x0537 | 38 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 8 |  |  |  |  | Setpoint | 0 | 157
4x0538 | 39 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 9 |  |  |  |  | Setpoint | 0 | 158
4x0539 | 40 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Torsdag | skift 10 |  |  |  |  | Setpoint | 0 | 159
4x0540 | 41 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 1 |  |  |  |  | Setpoint | 0 | 160
4x0541 | 42 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 2 |  |  |  |  | Setpoint | 0 | 161
4x0542 | 43 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 3 |  |  |  |  | Setpoint | 0 | 162
4x0543 | 44 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 4 |  |  |  |  | Setpoint | 0 | 163
4x0544 | 45 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 5 |  |  |  |  | Setpoint | 0 | 164
4x0545 | 46 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 6 |  |  |  |  | Setpoint | 0 | 165
4x0546 | 47 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 7 |  |  |  |  | Setpoint | 0 | 166
4x0547 | 48 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 8 |  |  |  |  | Setpoint | 0 | 167
4x0548 | 49 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 9 |  |  |  |  | Setpoint | 0 | 168
4x0549 | 50 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Fredag | skift 10 |  |  |  |  | Setpoint | 0 | 169
4x0550 | 51 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 1 |  |  |  |  | Setpoint | 0 | 170
4x0551 | 52 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 2 |  |  |  |  | Setpoint | 0 | 171
4x0552 | 53 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 3 |  |  |  |  | Setpoint | 0 | 172
4x0553 | 54 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 4 |  |  |  |  | Setpoint | 0 | 173
4x0554 | 55 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 5 |  |  |  |  | Setpoint | 0 | 174
4x0555 | 56 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 6 |  |  |  |  | Setpoint | 0 | 175
4x0556 | 57 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 7 |  |  |  |  | Setpoint | 0 | 176
4x0557 | 58 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 8 |  |  |  |  | Setpoint | 0 | 177
4x0558 | 59 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 9 |  |  |  |  | Setpoint | 0 | 178
4x0559 | 60 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Lørdag | skift 10 |  |  |  |  | Setpoint | 0 | 179
4x0560 | 61 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 1 |  |  |  |  | Setpoint | 0 | 180
4x0561 | 62 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 2 |  |  |  |  | Setpoint | 0 | 181
4x0562 | 63 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 3 |  |  |  |  | Setpoint | 0 | 182
4x0563 | 64 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 4 |  |  |  |  | Setpoint | 0 | 183
4x0564 | 65 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 5 |  |  |  |  | Setpoint | 0 | 184
4x0565 | 66 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 6 |  |  |  |  | Setpoint | 0 | 185
4x0566 | 67 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 7 |  |  |  |  | Setpoint | 0 | 186
4x0567 | 68 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 8 |  |  |  |  | Setpoint | 0 | 187
4x0568 | 69 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 9 |  |  |  |  | Setpoint | 0 | 188
4x0569 | 70 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min | Søndag | skift 10 |  |  |  |  | Setpoint | 0 | 189
Kalender Hastighed og reduktion | Eks. Speed x 256+Reduktion -> 1*256+100=256+100=356 | [5 empty] | Dag | Skift | Min Speed:0 Reduktion:0 | Min Speed:4 Reduktion:100 -> -10.0 °C |  |  | Type | Object | Adress
4x0600 | 1 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 1 |  |  |  |  | Setpoint | 0 | 190
4x0601 | 2 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 2 |  |  |  |  | Setpoint | 0 | 191
4x0602 | 3 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 3 |  |  |  |  | Setpoint | 0 | 192
4x0603 | 4 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 4 |  |  |  |  | Setpoint | 0 | 193
4x0604 | 5 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 5 |  |  |  |  | Setpoint | 0 | 194
4x0605 | 6 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 6 |  |  |  |  | Setpoint | 0 | 195
4x0606 | 7 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 7 |  |  |  |  | Setpoint | 0 | 196
4x0607 | 8 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 8 |  |  |  |  | Setpoint | 0 | 197
4x0608 | 9 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 9 |  |  |  |  | Setpoint | 0 | 198
4x0609 | 10 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Mandag | skift 10 |  |  |  |  | Setpoint | 0 | 199
4x0610 | 11 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 1 |  |  |  |  | Setpoint | 0 | 200
4x0611 | 12 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 2 |  |  |  |  | Setpoint | 0 | 201
4x0612 | 13 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 3 |  |  |  |  | Setpoint | 0 | 202
4x0613 | 14 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 4 |  |  |  |  | Setpoint | 0 | 203
4x0614 | 15 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 5 |  |  |  |  | Setpoint | 0 | 204
4x0615 | 16 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 6 |  |  |  |  | Setpoint | 0 | 205
4x0616 | 17 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 7 |  |  |  |  | Setpoint | 0 | 206
4x0617 | 18 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 8 |  |  |  |  | Setpoint | 0 | 207
4x0618 | 19 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 9 |  |  |  |  | Setpoint | 0 | 208
4x0619 | 20 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Tirsdag | skift 10 |  |  |  |  | Setpoint | 0 | 209
4x0620 | 21 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 1 |  |  |  |  | Setpoint | 0 | 210
4x0621 | 22 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 2 |  |  |  |  | Setpoint | 0 | 211
4x0622 | 23 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 3 |  |  |  |  | Setpoint | 0 | 212
4x0623 | 24 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 4 |  |  |  |  | Setpoint | 0 | 213
4x0624 | 25 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 5 |  |  |  |  | Setpoint | 0 | 214
4x0625 | 26 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 6 |  |  |  |  | Setpoint | 0 | 215
4x0626 | 27 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 7 |  |  |  |  | Setpoint | 0 | 216
4x0627 | 28 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 8 |  |  |  |  | Setpoint | 0 | 217
4x0628 | 29 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 9 |  |  |  |  | Setpoint | 0 | 218
4x0629 | 30 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Onsdag | skift 10 |  |  |  |  | Setpoint | 0 | 219
4x0630 | 31 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 1 |  |  |  |  | Setpoint | 0 | 220
4x0631 | 32 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 2 |  |  |  |  | Setpoint | 0 | 221
4x0632 | 33 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 3 |  |  |  |  | Setpoint | 0 | 222
4x0633 | 34 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 4 |  |  |  |  | Setpoint | 0 | 223
4x0634 | 35 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 5 |  |  |  |  | Setpoint | 0 | 224
4x0635 | 36 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 6 |  |  |  |  | Setpoint | 0 | 225
4x0636 | 37 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 7 |  |  |  |  | Setpoint | 0 | 226
4x0637 | 38 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 8 |  |  |  |  | Setpoint | 0 | 227
4x0638 | 39 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 9 |  |  |  |  | Setpoint | 0 | 228
4x0639 | 40 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Torsdag | skift 10 |  |  |  |  | Setpoint | 0 | 229
4x0640 | 41 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 1 |  |  |  |  | Setpoint | 0 | 230
4x0641 | 42 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 2 |  |  |  |  | Setpoint | 0 | 231
4x0642 | 43 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 3 |  |  |  |  | Setpoint | 0 | 232
4x0643 | 44 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 4 |  |  |  |  | Setpoint | 0 | 233
4x0644 | 45 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 5 |  |  |  |  | Setpoint | 0 | 234
4x0645 | 46 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 6 |  |  |  |  | Setpoint | 0 | 235
4x0646 | 47 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 7 |  |  |  |  | Setpoint | 0 | 236
4x0647 | 48 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 8 |  |  |  |  | Setpoint | 0 | 237
4x0648 | 49 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 9 |  |  |  |  | Setpoint | 0 | 238
4x0649 | 50 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Fredag | skift 10 |  |  |  |  | Setpoint | 0 | 239
4x0650 | 51 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 1 |  |  |  |  | Setpoint | 0 | 240
4x0651 | 52 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 2 |  |  |  |  | Setpoint | 0 | 241
4x0652 | 53 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 3 |  |  |  |  | Setpoint | 0 | 242
4x0653 | 54 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 4 |  |  |  |  | Setpoint | 0 | 243
4x0654 | 55 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 5 |  |  |  |  | Setpoint | 0 | 244
4x0655 | 56 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 6 |  |  |  |  | Setpoint | 0 | 245
4x0656 | 57 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 7 |  |  |  |  | Setpoint | 0 | 246
4x0657 | 58 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 8 |  |  |  |  | Setpoint | 0 | 247
4x0658 | 59 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 9 |  |  |  |  | Setpoint | 0 | 248
4x0659 | 60 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Lørdag | skift 10 |  |  |  |  | Setpoint | 0 | 249
4x0660 | 61 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 1 |  |  |  |  | Setpoint | 0 | 250
4x0661 | 62 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 2 |  |  |  |  | Setpoint | 0 | 251
4x0662 | 63 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 3 |  |  |  |  | Setpoint | 0 | 252
4x0663 | 64 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 4 |  |  |  |  | Setpoint | 0 | 253
4x0664 | 65 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 5 |  |  |  |  | Setpoint | 0 | 254
4x0665 | 66 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 6 |  |  |  |  | Setpoint | 0 | 255
4x0666 | 67 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 7 |  |  |  |  | Setpoint | 0 | 256
4x0667 | 68 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 8 |  |  |  |  | Setpoint | 0 | 257
4x0668 | 69 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 9 |  |  |  |  | Setpoint | 0 | 258
4x0669 | 70 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction | Søndag | skift 10 |  |  |  |  | Setpoint | 0 | 259

## Optima 301
Modbus protokol for ES950 Optima 301
Mode: | RTU | (MSB first)
Standard: | Modbus application protokol specification V1.1a Modbus over serial lin V1.02
WWW adresse | Modbus.org
Baud | 0=Modbus Off, 1=9600, 2=19200 | default | 0
Start bits | 1 | default | 1
Data bits | 8 | default | 8
Stop Bits | 1 | default | 1
Parity | Even | default | Even
Address | 1-247 | default | 1
Registers Map
Support function | 1,2,3,4,5,6,17
Register number | Data description | R/W | Length | Units | Valid response | Remarks
0x0000 | Relay 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0001 | Relay 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0002 | Relay 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0003 | Relay 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0004 | Relay 5 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0005 | Relay 6 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0006 | Relay 7 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0007 | Relay 8 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0008 | Relay 9 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0009 | Relay 10 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0010 | Relay 11 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0011 | Not Used Digital out 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0012 | Not Used Digital out 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0013 | Not Used Digital out 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0014 | Not Used Digital out 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0000 | Hygrostat | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0001 | Start/stop | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0002 | Not Used Digital in1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0003 | Not Used Digital in2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0004 | Not Used Digital in3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0005 | Not Used Digital in4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
3x0000 | T1 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0001 | T2 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0002 | T3 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0003 | T4 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0004 | T5 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0005 | T6 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0006 | T7 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0007 | T8 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0008 | T9 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0009 | T2 Panel | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0101 | Alarm | R | 1 | UINT16 | Bits
3x0102 | Inlet fan | R |  | UINT16 | 0-100%
3x0103 | Extract fan | R | 1 | UINT16 | 0-100%
3x0104 | Bypass | R | 1 | UINT16 | 0-100%
3x0105 | Watervalve | R | 1 | UINT16 | 0-100%
3x0106 | Not Used volt1 | R | 1 | UINT16 | 0-1000 (0-10V) | 0-10V output
3x0107 | Not Used volt2 | R | 1 | UINT16 | 0-1000 (0-10V) | 0-10V output
3x0108 | Inlet fan RPM | R | 1 | UINT16 | 0-9999
3x0109 | Extract fan RPM | R | 1 | UINT16 | 0-9999
3x0200 | Programme Version Controller | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0201 | Programme Version Display | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0202 | Sub Version Controller | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0203 | Sub Version Display | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0204 | ModbusVersion | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0205 | Sub ModbusVersion | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
[11 empty] | Display | Display
Group0 | [6 empty] | Min | Max | Offset | Resolution | Min+offset | Max+offset
4x0000 | 01) Temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 200 | 100 | 0.1 | 10 | 30
4x0001 | 02) Cooling (°C) | R/W | 1 | UINT16 |  |  | 30 | 100 | 0 | 0.1 | 3 | 10
4x0002 | 03) Cooling (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0003 | 04) Hour level 3-4 (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0004 | 05) Filter change (mon) | R/W | 1 | UINT16 |  |  | 0 | 6 | 0 | 1 | 0 | 6
4x0005 | 06) Ovndrift timer (timer) | R/W | 1 | UINT16 |  |  | 0 | 20 | 0 | 1 | 0 | 20
4x0006 | 10) Level 1 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0007 | 11) Level 2 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0008 | 12) Level 3 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0009 | 13) Level 1 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0010 | 14) Level 2 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0011 | 15) Level 3 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0012 | 16) T2 adjustment (°C) | R/W | 1 | UINT16 |  |  | 0 | 50 | -50 | 0.1 | -5 | 0
4x0013 | 17) Level 3-4 (hour) | R/W | 1 | UINT16 |  |  | 1 | 9 | 0 | 1 | 1 | 9
4x0014 | 18) Filter change autostop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0015 | 19) Regform (0=Rum,1=indbl, 2=udsug) | R/W | 1 | UINT16 |  |  | 0 | 2 | 0 | 1 | 0 | 2
4x0016 | 20) Preheat (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0017 | 21) Preheat temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | -150 | 0.1 | -15 | 0
4x0018 | 22) Water regulator interval (sec) | R/W | 1 | UINT16 |  |  | 1 | 250 | 0 | 1 | 1 | 250
4x0019 | 23) Power regulator interval (min) | R/W | 1 | UINT16 |  |  | 1 | 30 | 0 | 1 | 1 | 30
4x0020 | 24) Min air volume (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0021 | 25) Frost (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0022 | 26) Frost default (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0023 | 27) Aux. relay R9 | R/W | 1 | UINT16 |  |  | 0 | 6 | 0 | 1 | 0 | 6
4x0024 | 28) Unit stop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0025 | 29) Stop defrost (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | 0 | 0.1 | 0 | 15
4x0026 | 30) Compressor differens (°C) | R/W | 1 | UINT16 |  |  | 1 | 10 | 0 | 0.1 | 0.1 | 1
4x0027 | 31) Constant (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0028 | 32) Constant (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0029 | 33) Reduction (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0030 | 34) Reduce supply (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | -150 | 0.1 | -15 | 0
4x0031 | 35) Reduce supply speed (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0032 | 36) Min external cool (°C) | R/W | 1 | UINT16 |  |  | 0 | 20 | 0 | 1 | 0 | 20
4x0033 | 37) Reheat (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0034 | 38) Prehaet supply (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0035 | 39) Prehaet supply temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 250 | -250 | 0.1 | -25 | 0
4x0036 | 40) Bedroom temperature (°C) | R/W | 1 | UINT16 |  |  | 10 | 25 | 0 | 1 | 10 | 25
4x0037 | 41) Fire Mode (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0038 | 42) Fire/Filter mode (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0039 | 43) Ekstra filter timer (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0040 | 44) Speed differens (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0041 | 45) Modbus mode (0=OFF, 1=9600, 2=19200) | R/W | 1 | UINT16 |  | 0=Modbus Off, 1=9600, 2=19200 | 0 | 2 | 0 | 1 | 0 | 2
4x0042 | 46) Modbus address | R/W | 1 | UINT16 |  |  | 1 | 247 | 0 | 1 | 1 | 247
4x0043 | 47) Afrim ventilator hastighed (%) | R/W | 1 | UINT16 |  |  | 0 | 40 | 0 | 1 | 0 | 40
4x0044 | 48) Service mode (0=OFF, 1=Vent1, 2, 3, 4) | R/W | 1 | UINT16 |  |  | 0 | 4 | 0 | 1 | 0 | 4
4x0045
4x0046
4x0047
4x0048
4x0049
4x0050
4x0051
4x0052
4x0053
4x0054
4x0055
4x0056
4x0057
4x0058
4x0059
Group1
4x0100 | Panel fan mode speed switch | R/W | 1 | UINT16 | 0-4 | 0=Off, 1=S1, 2=S2, 3=S3, 4=S4
4x0105 | Common ResetFilter | R/W | 1 | UINT16 | 0-1 | 1=reset filter
Group2
4x0200 | Hour | R/W |  | UINT16 | 0-23
4x0201 | Minute | R/W |  | UINT16 | 0-59
4x0202 | Day | R/W |  | UINT16 | 1-7
4x0203 | Date | R/W |  | UINT16 | 1-31
4x0204 | Month | R/W |  | UINT16 | 1-12
4x0205 | Year | R/W |  | UINT16 | 0-99 | 0= jahr 2000
Group3
4x0500 | 1 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0501 | 2 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0502 | 3 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0503 | 4 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0504 | 5 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0505 | 6 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0506 | 7 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0507 | 8 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0508 | 9 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0509 | 10 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0510 | 11 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0511 | 12 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0512 | 13 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0513 | 14 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0514 | 15 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0515 | 16 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0516 | 17 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0517 | 18 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0518 | 19 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0519 | 20 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0520 | 21 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0521 | 22 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0522 | 23 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0523 | 24 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0524 | 25 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0525 | 26 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0526 | 27 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0527 | 28 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0528 | 29 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0529 | 30 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0530 | 31 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0531 | 32 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0532 | 33 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0533 | 34 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0534 | 35 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0535 | 36 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0536 | 37 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0537 | 38 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0538 | 39 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0539 | 40 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0540 | 41 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0541 | 42 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0542 | 43 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0543 | 44 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0544 | 45 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0545 | 46 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0546 | 47 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0547 | 48 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0548 | 49 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0549 | 50 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0550 | 51 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0551 | 52 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0552 | 53 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0553 | 54 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0554 | 55 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0555 | 56 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0556 | 57 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0557 | 58 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0558 | 59 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0559 | 60 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0560 | 61 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0561 | 62 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0562 | 63 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0563 | 64 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0564 | 65 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0565 | 66 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0566 | 67 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0567 | 68 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0568 | 69 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0569 | 70 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
Group4
4x0600 | 1 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0601 | 2 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0602 | 3 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0603 | 4 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0604 | 5 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0605 | 6 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0606 | 7 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0607 | 8 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0608 | 9 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0609 | 10 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0610 | 11 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0611 | 12 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0612 | 13 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0613 | 14 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0614 | 15 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0615 | 16 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0616 | 17 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0617 | 18 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0618 | 19 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0619 | 20 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0620 | 21 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0621 | 22 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0622 | 23 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0623 | 24 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0624 | 25 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0625 | 26 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0626 | 27 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0627 | 28 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0628 | 29 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0629 | 30 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0630 | 31 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0631 | 32 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0632 | 33 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0633 | 34 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0634 | 35 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0635 | 36 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0636 | 37 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0637 | 38 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0638 | 39 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0639 | 40 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0640 | 41 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0641 | 42 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0642 | 43 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0643 | 44 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0644 | 45 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0645 | 46 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0646 | 47 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0647 | 48 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0648 | 49 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0649 | 50 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0650 | 51 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0651 | 52 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0652 | 53 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0653 | 54 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0654 | 55 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0655 | 56 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0656 | 57 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0657 | 58 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0658 | 59 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0659 | 60 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0660 | 61 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0661 | 62 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0662 | 63 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0663 | 64 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0664 | 65 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0665 | 66 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0666 | 67 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0667 | 68 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0668 | 69 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0669 | 70 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
Group5
4x0700 | 1 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0701 | 2 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0702 | 3 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0703 | 4 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0704 | 5 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0705 | 6 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0706 | 7 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0707 | 8 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0708 | 9 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0709 | 10 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0710 | 11 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0711 | 12 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0712 | 13 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0713 | 14 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0714 | 15 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0715 | 16 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0716 | 17 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0717 | 18 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0718 | 19 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0719 | 20 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface

## Optima 310
Modbus protokol for ES950 Optima 310
Mode: | RTU | (MSB first)
Standard: | Modbus application protokol specification V1.1a Modbus over serial lin V1.02
WWW adresse | Modbus.org
Baud | 0=Modbus Off, 1=9600, 2=19200 | default | 0
Start bits | 1 | default | 1
Data bits | 8 | default | 8
Stop Bits | 1 | default | 1
Parity | Even | default | Even
Address | 1-247 | default | 1
Registers Map
Support function | 1,2,3,4,5,6,17
Register number | Data description | R/W | Length | Units | Valid response | Remarks
0x0000 | Relay 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0001 | Relay 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0002 | Relay 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0003 | Relay 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0004 | Relay 5 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0005 | Relay 6 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0006 | Relay 7 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0007 | Relay 8 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0008 | Relay 9 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0009 | Relay 10 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0010 | Relay 11 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0011 | Not Used Digital out 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0012 | Not Used Digital out 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0013 | Not Used Digital out 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0014 | Not Used Digital out 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0000 | Hygrostat | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0001 | Start/stop | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0002 | Not Used Digital in1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0003 | Not Used Digital in2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0004 | Not Used Digital in3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0005 | Not Used Digital in4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
3x0000 | T1 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0001 | T2 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0002 | T3 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0003 | T4 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0004 | T5 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0005 | T6 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0006 | T7 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0007 | T8 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0008 | T9 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0009 | T2 Panel | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0101 | Alarm | R | 1 | UINT16 | Bits
3x0102 | Inlet fan | R |  | UINT16 | 0-100%
3x0103 | Extract fan | R | 1 | UINT16 | 0-100%
3x0104 | Bypass | R | 1 | UINT16 | 0-100%
3x0105 | Watervalve | R | 1 | UINT16 | 0-100%
3x0106 | Not Used volt1 | R | 1 | UINT16 | 0-1000 (0-10V) | 0-10V output
3x0107 | Not Used volt2 | R | 1 | UINT16 | 0-1000 (0-10V) | 0-10V output
3x0108 | Inlet fan RPM | R | 1 | UINT16 | 0-9999
3x0109 | Extract fan RPM | R | 1 | UINT16 | 0-9999
3x0200 | Programme Version Controller | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0201 | Programme Version Display | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0202 | Sub Version Controller | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0203 | Sub Version Display | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0204 | ModbusVersion | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0205 | Sub ModbusVersion | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
[11 empty] | Display | Display
Group0 | [6 empty] | Min | Max | Offset | Resolution | Min+offset | Max+offset
4x0000 | 01) Temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 200 | 100 | 0.1 | 10 | 30
4x0001 | 02) Domestic hot water temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 550 | 0 | 0.1 | 0 | 55
4x0002 | 03) Power-patron ON (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0003 | 04) Hour level 3-4 (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0004 | 05) Filter change (mon) | R/W | 1 | UINT16 |  |  | 0 | 6 | 0 | 1 | 0 | 6
4x0005 |  | R/W | 1 | UINT16 |  |  | 0 | 0 | 0 | 1 | 0 | 0
4x0006 | 10) Level 1 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0007 | 11) Level 2 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0008 | 12) Level 3 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0009 | 13) Level 1 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0010 | 14) Level 2 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0011 | 15) Level 3 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0012 | 16) T2 adjustment (°C) | R/W | 1 | UINT16 |  |  | 0 | 50 | -50 | 0.1 | -5 | 0
4x0013 | 17) Level 3-4 (hour) | R/W | 1 | UINT16 |  |  | 1 | 9 | 0 | 1 | 1 | 9
4x0014 | 18) Filter change autostop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0015 | 19) Power-patron (°C) | R/W | 1 | UINT16 |  |  | 0 | 650 | 0 | 0.1 | 0 | 65
4x0016 | 20) Disinfection (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0017 | 21) Domestic hot water/air (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0018 | 22) Water reg interval (sec) | R/W | 1 | UINT16 |  |  | 1 | 250 | 0 | 1 | 1 | 250
4x0019 | 23) Power reg interval (min) | R/W | 1 | UINT16 |  |  | 1 | 30 | 0 | 1 | 1 | 30
4x0020 | 24) Min air volume (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0021 | 25) Reheat (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0022 | 26) Sun collector (°C) | R/W | 1 | UINT16 |  |  | 0 | 50 | 0 | 0.1 | 0 | 5
4x0023 | 27) Aux. Relay R9 | R/W | 1 | UINT16 |  |  | 0 | 5 | 0 | 1 | 0 | 5
4x0024 | 28) Unit stop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0025 | 29) Stop defrost (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | 0 | 0.1 | 0 | 15
4x0026 | 30) Compressor differens (°C) | R/W | 1 | UINT16 |  |  | 1 | 10 | 0 | 0.1 | 0.1 | 1
4x0027 | 31) Constant (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0028 | 32) Constant (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0029 | 33) Reduction (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0030 | 34) Reduce supply (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | -150 | 0.1 | -15 | 0
4x0031 | 35) Reduce supply speed (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0032 | 36) Aux. relay R8 | R/W | 1 | UINT16 |  |  | 0 | 3 | 0 | 1 | 0 | 3
4x0033 | 37) Earth collector temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0034 | 38) Print version (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0035 | 39) Modbus mode (0=OFF, 1=9600, 2=19200) | R/W | 1 | UINT16 |  | 0=Modbus Off, 1=9600, 2=19200 | 0 | 2 | 0 | 1 | 0 | 2
4x0036 | 40) Modbus address | R/W | 1 | UINT16 |  |  | 1 | 247 | 0 | 1 | 1 | 247
4x0037 |  | R/W | 1 | UINT16
4x0038 |  | R/W | 1 | UINT16
4x0039 |  | R/W | 1 | UINT16
4x0040 |  | R/W | 1 | UINT16
4x0041 |  | R/W | 1 | UINT16
4x0042 |  | R/W | 1 | UINT16
4x0043 |  | R/W | 1 | UINT16
4x0044 |  | R/W | 1 | UINT16
4x0045
4x0046
4x0047
4x0048
4x0049
4x0050
4x0051
4x0052
4x0053
4x0054
4x0055
4x0056
4x0057
4x0058
4x0059
Group1
4x0100 | Panel fan mode speed switch | R/W | 1 | UINT16 | 0-4 | 0=Off, 1=S1, 2=S2, 3=S3, 4=S4
4x0105 | Common ResetFilter | R/W | 1 | UINT16 | 0-1 | 1=reset filter
Group2
4x0200 | Hour | R/W |  | UINT16 | 0-23
4x0201 | Minute | R/W |  | UINT16 | 0-59
4x0202 | Day | R/W |  | UINT16 | 1-7
4x0203 | Date | R/W |  | UINT16 | 1-31
4x0204 | Month | R/W |  | UINT16 | 1-12
4x0205 | Year | R/W |  | UINT16 | 0-99 | 0= jahr 2000
Group3
4x0500 | 1 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0501 | 2 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0502 | 3 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0503 | 4 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0504 | 5 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0505 | 6 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0506 | 7 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0507 | 8 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0508 | 9 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0509 | 10 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0510 | 11 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0511 | 12 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0512 | 13 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0513 | 14 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0514 | 15 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0515 | 16 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0516 | 17 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0517 | 18 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0518 | 19 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0519 | 20 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0520 | 21 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0521 | 22 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0522 | 23 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0523 | 24 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0524 | 25 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0525 | 26 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0526 | 27 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0527 | 28 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0528 | 29 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0529 | 30 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0530 | 31 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0531 | 32 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0532 | 33 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0533 | 34 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0534 | 35 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0535 | 36 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0536 | 37 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0537 | 38 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0538 | 39 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0539 | 40 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0540 | 41 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0541 | 42 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0542 | 43 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0543 | 44 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0544 | 45 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0545 | 46 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0546 | 47 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0547 | 48 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0548 | 49 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0549 | 50 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0550 | 51 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0551 | 52 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0552 | 53 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0553 | 54 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0554 | 55 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0555 | 56 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0556 | 57 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0557 | 58 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0558 | 59 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0559 | 60 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0560 | 61 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0561 | 62 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0562 | 63 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0563 | 64 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0564 | 65 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0565 | 66 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0566 | 67 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0567 | 68 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0568 | 69 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0569 | 70 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
Group4
4x0600 | 1 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0601 | 2 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0602 | 3 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0603 | 4 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0604 | 5 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0605 | 6 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0606 | 7 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0607 | 8 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0608 | 9 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0609 | 10 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0610 | 11 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0611 | 12 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0612 | 13 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0613 | 14 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0614 | 15 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0615 | 16 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0616 | 17 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0617 | 18 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0618 | 19 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0619 | 20 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0620 | 21 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0621 | 22 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0622 | 23 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0623 | 24 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0624 | 25 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0625 | 26 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0626 | 27 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0627 | 28 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0628 | 29 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0629 | 30 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0630 | 31 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0631 | 32 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0632 | 33 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0633 | 34 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0634 | 35 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0635 | 36 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0636 | 37 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0637 | 38 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0638 | 39 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0639 | 40 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0640 | 41 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0641 | 42 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0642 | 43 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0643 | 44 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0644 | 45 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0645 | 46 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0646 | 47 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0647 | 48 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0648 | 49 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0649 | 50 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0650 | 51 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0651 | 52 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0652 | 53 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0653 | 54 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0654 | 55 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0655 | 56 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0656 | 57 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0657 | 58 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0658 | 59 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0659 | 60 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0660 | 61 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0661 | 62 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0662 | 63 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0663 | 64 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0664 | 65 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0665 | 66 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0666 | 67 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0667 | 68 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0668 | 69 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0669 | 70 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
Group5
4x0700 | 1 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0701 | 2 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0702 | 3 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0703 | 4 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0704 | 5 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0705 | 6 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0706 | 7 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0707 | 8 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0708 | 9 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0709 | 10 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0710 | 11 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0711 | 12 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0712 | 13 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0713 | 14 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0714 | 15 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0715 | 16 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0716 | 17 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0717 | 18 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0718 | 19 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0719 | 20 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface

## Optima 311-312
Modbus protokol for ES950 Optima 311
Mode: | RTU | (MSB first)
Standard: | Modbus application protokol specification V1.1a Modbus over serial lin V1.02
WWW adresse | Modbus.org
Baud | 0=Modbus Off, 1=9600, 2=19200 | default | 0
Start bits | 1 | default | 1
Data bits | 8 | default | 8
Stop Bits | 1 | default | 1
Parity | Even | default | Even
Address | 1-247 | default | 1
Registers Map
Support function | 1,2,3,4,5,6,17
Register number | Data description | R/W | Length | Units | Valid response | Remarks
0x0000 | Relay 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0001 | Relay 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0002 | Relay 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0003 | Relay 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0004 | Relay 5 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0005 | Relay 6 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0006 | Relay 7 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0007 | Relay 8 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0008 | Relay 9 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0009 | Relay 10 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0010 | Relay 11 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0011 | Not Used Digital out 1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0012 | Not Used Digital out 2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0013 | Not Used Digital out 3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
0x0014 | Not Used Digital out 4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0000 | Hygrostat | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0001 | Start/stop | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0002 | Not Used Digital in1 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0003 | Not Used Digital in2 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0004 | Not Used Digital in3 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
1x0005 | Not Used Digital in4 | R | 1 | UINT16 | ON/OFF | 0=OFF 1=ON
3x0000 | T1 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0001 | T2 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0002 | T3 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0003 | T4 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0004 | T5 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0005 | T6 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0006 | T7 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0007 | T8 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0008 | T9 | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0009 | T2 Panel | R | 1 | UINT16 | -30grdC - 70grd C | 300=0.0°C
3x0101 | Alarm | R | 1 | UINT16 | Bits
3x0102 | Inlet fan | R |  | UINT16 | 0-100%
3x0103 | Extract fan | R | 1 | UINT16 | 0-100%
3x0104 | Bypass | R | 1 | UINT16 | 0-100%
3x0105 | Watervalve | R | 1 | UINT16 | 0-100%
3x0106 | Not Used volt1 | R | 1 | UINT16 | 0-1000 (0-10V) | 0-10V output
3x0107 | Not Used volt2 | R | 1 | UINT16 | 0-1000 (0-10V) | 0-10V output
3x0108 | Inlet fan RPM | R | 1 | UINT16 | 0-9999
3x0109 | Extract fan RPM | R | 1 | UINT16 | 0-9999
3x0200 | Programme Version Controller | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0201 | Programme Version Display | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0202 | Sub Version Controller | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0203 | Sub Version Display | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
3x0204 | ModbusVersion | R | 1 | UINT16 | 0-9999 | 1=0.1
3x0205 | Sub ModbusVersion | R | 1 | UINT16 | 0-9999 | ascii 97=a, 98=b
[11 empty] | Display | Display
Group0 | [6 empty] | Min | Max | Offset | Resolution | Min+offset | Max+offset
4x0000 | 01) Temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 200 | 100 | 0.1 | 10 | 30
4x0001 | 02) Domestic hot water temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 550 | 0 | 0.1 | 0 | 55
4x0002 | 03) Power-patron ON (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0003 | 04) Hour level 3-4 (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0004 | 05) Filter change (mon) | R/W | 1 | UINT16 |  |  | 0 | 6 | 0 | 1 | 0 | 6
4x0005 |  | R/W | 1 | UINT16 |  |  | 0 | 0 | 0 | 1 | 0 | 0
4x0006 | 10) Level 1 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0007 | 11) Level 2 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0008 | 12) Level 3 supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0009 | 13) Level 1 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0010 | 14) Level 2 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0011 | 15) Level 3 extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0012 | 16) T2 adjustment (°C) | R/W | 1 | UINT16 |  |  | 0 | 50 | -50 | 0.1 | -5 | 0
4x0013 | 17) Level 3-4 (hour) | R/W | 1 | UINT16 |  |  | 1 | 9 | 0 | 1 | 1 | 9
4x0014 | 18) Filter change autostop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0015 | 19) Power-patron (°C) | R/W | 1 | UINT16 |  |  | 0 | 650 | 0 | 0.1 | 0 | 65
4x0016 | 20) Disinfection (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0017 | 21) Domestic hot water/air (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0018 | 22) Water reg interval (sec) | R/W | 1 | UINT16 |  |  | 1 | 250 | 0 | 1 | 1 | 250
4x0019 | 23) Power reg interval (min) | R/W | 1 | UINT16 |  |  | 1 | 30 | 0 | 1 | 1 | 30
4x0020 | 24) Min air volume extract (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0021 | 25) Reheat (on/off) | R/W | 1 | UINT16 |  |  | 0 | 2 | 0 | 1 | 0 | 2
4x0022 | 26) Sun collector (°C) | R/W | 1 | UINT16 |  |  | 0 | 50 | 0 | 0.1 | 0 | 5
4x0023 | 27) Aux. Relay R9 | R/W | 1 | UINT16 |  |  | 0 | 5 | 0 | 1 | 0 | 5
4x0024 | 28) Unit stop (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0025 | 29) Stop defrost (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | 0 | 0.1 | 0 | 15
4x0026 | 30) Compressor differens (°C) | R/W | 1 | UINT16 |  |  | 1 | 10 | 0 | 0.1 | 0.1 | 1
4x0027 | 31) Constant (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0028 | 32) Constant (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0029 | 33) Reduction (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0030 | 34) Reduce supply (°C) | R/W | 1 | UINT16 |  |  | 0 | 150 | -150 | 0.1 | -15 | 0
4x0031 | 35) Reduce supply speed (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0032 | 36) Aux. relay R8 | R/W | 1 | UINT16 |  |  | 0 | 3 | 0 | 1 | 0 | 3
4x0033 | 37) Earth collector temperature (°C) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 0.1 | 0 | 10
4x0034 | 38) Print version (on/off) | R/W | 1 | UINT16 |  |  | 0 | 1 | 0 | 1 | 0 | 1
4x0035 | 39) Min air volume supply (%) | R/W | 1 | UINT16 |  |  | 0 | 100 | 0 | 1 | 0 | 100
4x0036 | 40) Min air volume mode | R/W | 1 | UINT16 |  |  | 0 | 3 | 0 | 1 | 0 | 3
4x0037 | 41) Modbus mode (0=OFF, 1=9600, 2=19200) | R/W | 1 | UINT16 |  | 0=Modbus Off, 1=9600, 2=19200 | 0 | 2 | 0 | 1 | 0 | 2
4x0038 | 42) Modbus address | R/W | 1 | UINT16 |  |  | 1 | 247 | 0 | 1 | 1 | 247
4x0039 |  | R/W | 1 | UINT16
4x0040 |  | R/W | 1 | UINT16
4x0041 |  | R/W | 1 | UINT16
4x0042 |  | R/W | 1 | UINT16
4x0043 |  | R/W | 1 | UINT16
4x0044 |  | R/W | 1 | UINT16
4x0045
4x0046
4x0047
4x0048
4x0049
4x0050
4x0051
4x0052
4x0053
4x0054
4x0055
4x0056
4x0057
4x0058
4x0059
Group1
4x0100 | Panel fan mode speed switch | R/W | 1 | UINT16 | 0-4 | 0=Off, 1=S1, 2=S2, 3=S3, 4=S4
4x0105 | Common ResetFilter | R/W | 1 | UINT16 | 0-1 | 1=reset filter
Group2
4x0200 | Hour | R/W |  | UINT16 | 0-23
4x0201 | Minute | R/W |  | UINT16 | 0-59
4x0202 | Day | R/W |  | UINT16 | 1-7
4x0203 | Date | R/W |  | UINT16 | 1-31
4x0204 | Month | R/W |  | UINT16 | 1-12
4x0205 | Year | R/W |  | UINT16 | 0-99 | 0= jahr 2000
Group3
4x0500 | 1 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0501 | 2 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0502 | 3 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0503 | 4 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0504 | 5 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0505 | 6 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0506 | 7 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0507 | 8 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0508 | 9 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0509 | 10 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0510 | 11 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0511 | 12 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0512 | 13 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0513 | 14 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0514 | 15 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0515 | 16 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0516 | 17 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0517 | 18 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0518 | 19 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0519 | 20 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0520 | 21 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0521 | 22 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0522 | 23 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0523 | 24 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0524 | 25 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0525 | 26 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0526 | 27 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0527 | 28 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0528 | 29 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0529 | 30 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0530 | 31 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0531 | 32 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0532 | 33 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0533 | 34 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0534 | 35 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0535 | 36 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0536 | 37 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0537 | 38 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0538 | 39 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0539 | 40 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0540 | 41 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0541 | 42 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0542 | 43 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0543 | 44 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0544 | 45 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0545 | 46 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0546 | 47 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0547 | 48 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0548 | 49 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0549 | 50 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0550 | 51 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0551 | 52 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0552 | 53 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0553 | 54 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0554 | 55 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0555 | 56 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0556 | 57 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0557 | 58 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0558 | 59 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0559 | 60 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0560 | 61 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0561 | 62 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0562 | 63 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0563 | 64 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0564 | 65 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0565 | 66 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0566 | 67 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0567 | 68 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0568 | 69 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
4x0569 | 70 Calendar change merged hour+Min | R/W | 1 | UINT16 |  | HB:Hour LB:Min
Group4
4x0600 | 1 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0601 | 2 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0602 | 3 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0603 | 4 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0604 | 5 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0605 | 6 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0606 | 7 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0607 | 8 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0608 | 9 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0609 | 10 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0610 | 11 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0611 | 12 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0612 | 13 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0613 | 14 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0614 | 15 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0615 | 16 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0616 | 17 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0617 | 18 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0618 | 19 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0619 | 20 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0620 | 21 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0621 | 22 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0622 | 23 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0623 | 24 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0624 | 25 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0625 | 26 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0626 | 27 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0627 | 28 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0628 | 29 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0629 | 30 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0630 | 31 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0631 | 32 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0632 | 33 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0633 | 34 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0634 | 35 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0635 | 36 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0636 | 37 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0637 | 38 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0638 | 39 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0639 | 40 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0640 | 41 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0641 | 42 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0642 | 43 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0643 | 44 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0644 | 45 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0645 | 46 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0646 | 47 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0647 | 48 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0648 | 49 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0649 | 50 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0650 | 51 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0651 | 52 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0652 | 53 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0653 | 54 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0654 | 55 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0655 | 56 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0656 | 57 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0657 | 58 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0658 | 59 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0659 | 60 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0660 | 61 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0661 | 62 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0662 | 63 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0663 | 64 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0664 | 65 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0665 | 66 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0666 | 67 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0667 | 68 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0668 | 69 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
4x0669 | 70 Calendar change merged Speed+Reduction | R/W | 1 | UINT16 |  | HB: Speed LB: Reduction
Group5
4x0700 | 1 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0701 | 2 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0702 | 3 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0703 | 4 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0704 | 5 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0705 | 6 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0706 | 7 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0707 | 8 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0708 | 9 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0709 | 10 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0710 | 11 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0711 | 12 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0712 | 13 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0713 | 14 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0714 | 15 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0715 | 16 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0716 | 17 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0717 | 18 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0718 | 19 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface
4x0719 | 20 Defrost program merged Before cooling surface+Cooling surface | R/W | 1 | UINT16 |  | HB:Before cooling LB:cooling surface

## Alarm-Status
Alarms / Status | Dec | OPT 250 | OPT 251 | OPT 260 | OPT 300 | OPT 301 (OPT 300) | OPT 311 | OPT 312 | HVPC
bit0 | 1 | - | Føler fejl | Føler fejl | - | - | - | - | EC motor error
bit1 | 2 | - | - | Bypass ON/OFF | - | - | - | - | Ekstra filter alarm
bit2 | 4 | - | Relay R9 | Relay R9 | - | - | - | - | Drift relæ R9
bit3 | 8 | - | - | Filter fejl | - | - | - | - | Filter alarm
bit4 | 16 | Vandfrost | Vandfrost | Vandfrost fejl | Vandfrost | Vandfrost | - | - | Vandfrost
bit5 | 32 | - | - | - | Pressostat | Pressostat | Pressostat | Pressostat | Pressostat
bit6 | 64 | Hygrostat | Hygrostat | Hygrostat | Hygrostat | Hygrostat | Hygrostat | Hygrostat | Hygrostat
bit7 | 128 | Reset Filter | Reset Filter | Anlæg stop | Reset Filter | Reset Filter | Reset Filter | Reset Filter | Reset Filter
bit8 | 256 | - | - | - | Afrimning | Afrimning | Afrimning | Afrimning | Afrimning R4
bit9 | 512 | - | - | - | El-trin B | El-trin B | Brugsvand | Brugsvand | PTC1 R5
bit10 | 1024 | - | Bypass / køl | Bypass ON/OFF | El-trin C | El-trin C | Rumvarme | Rumvarme | PTC2 R6
bit11 | 2048 | - | - | - | El-trin D | El-trin D | - | - | Komp ON + Heat ON R7
bit12 | 4096 | Drift | Drift R8 | Drift R8 | Køling | Køling | R8-sol/pump/drift | R8-sol/pump/drift | Køling R8
bit13 | 8192 | El-eftervarme | El-eftervarme R3 | El-eftervarme R2 | El-trin A | El-trin A | Elvarme vand | Elvarme vand | Eftervarme R2
bit14 | 16384 | Ekstra køl | El-forvarme R2 | EL-forvarme R3 | Ekstra køl | Ekstra køl | Indblæs ekstra varme | Indblæs ekstra varme | Forvarme R3
bit15 | 32768 | - | - |  | Kompressor | Kompressor | Kompressor | Kompressor | Kompressor R1